## Slide 2: Introduction to PID Control
Brad Schofield, BE ICS AP

## Slide 3: https://www.youtube.com/watch?v=ng2PVOePN68

## Slide 4: Course plan
09:00-10:00: What is PID control?
10:00-10:30: The UNICOS PID controller
10:30-10:45: Coffee
10:45-11:15: Manual tuning
11:15-12:00: Manual tuning exercise
12:00-14:00: Lunch
14:00-15:00: Autotuning
15:00-16:00: Autotuning exercise
16:00-16:15: Coffee
16:15-17:00: Questions & Wrap-up

## Slide 5: What is PID Control?
Let’s take a step back… What is control?
Control is just making a dynamic process behave in the way we want
We need 3 things to do this:
  A way to influence the process
  A way to see how the process behaves
  A way to define how we want it to behave

## Slide 6: Defining behaviour
We usually specify a value we want some output of the system to have
  Usually called the Setpoint (SP)
Can be the temperature of a room, the level in a tank, the flow rate in a pipe…
The value can be fixed, or may change with time…

## Slide 7: Influencing the process
We need some kind of control input which can create changes in the behavior of the process
Can be a heater, a valve, a pump…
Typically it is not the same physical quantity as what we are controlling

## Slide 8: Observing behavior
If we knew exactly how the process worked, we would know what the output would be for a given control input…
Most of the time we don’t know exactly, so we need to measure what the process does
  Usually called Measured Variable (MV) or Process Variable (PV)

## Slide 9: Feedback Control
Now we have a measurement (MV), some value that we want it to be (SP), and some way to make changes to the process (control input)
We can ‘close the loop’

## Slide 10: The Controller as a System
Now we can see that any controller can be thought of as a system that takes a setpoint and a measured value as inputs, and gives a control signal as an output
Controller
SP
MV
Control

## Slide 11: The Controller as a System
The controller needs to convert two signals of one physical quantity (such as temperature) into one signal of another (such as valve position)
Controller
SP
MV
Control

## Slide 12: The Controller as a System
We know that the process is a dynamic system:
  Its outputs depend on current inputs as well as its past state
For the controller to deal with this, it makes sense that it should be a dynamic system too

## Slide 13: The Error Signal
Very often we can think of the controller acting on the difference between SP and MV:
Controller
SP
MV
Control
+
-
Error
Σ

## Slide 14: The Closed Loop
This is the ‘classic’ closed loop block diagram representation of a control system
Controller
SP
MV
+
-
e
Σ
Process
u

## Slide 15: A Dynamic Controller
We said that since the process is dynamic (dependent on inputs made at different times), it makes sense that the controller should be too
How do we usually think of time?
  ‘Present’
  ‘Past’
  ‘Future’

## Slide 16: Splitting the Controller
SP
MV
+
-
e
Σ
Process
Future
Past
Present
u

## Slide 17: The ‘Present’
This part of the controller is only concerned with what the error is now
Let’s take a simple law: let the control signal be proportional to the error:

## Slide 18: Proportional Control
This is what is referred to as proportional control. The control action at any instant is the same as a constant times the error at the same instant
The constant is the Proportional Gain, and is the first of our controller’s parameters

## Slide 19: Proportional Control
SP
MV
+
-
e
Σ
Process
Future
Past
Proportional
u

## Slide 20: Is Proportional Control enough?
Intuitively it seems like it should be fine on its own: when the error is big, the control input is big to correct it. As the error reduced so does the control input.
But there are problems…

## Slide 21: Problem 1
Think of a pendulum.
If the setpoint is hanging straight down, then gravity acts as a proportional controller for the position…
Pendulum will oscillate!

## Slide 22: Problem 2
What happens when the error is zero?
Control input is zero.
Causes problems if we need to have a nonzero control value while at our setpoint

## Slide 23: Problem 2: steady state error
This problem is normally called steady state error
It’s a confusing name. The issue is just that the controller can’t produce any output when the error is zero.
Easiest to see for tank level control: If there is a constant flow out of the tank, the controller must provide the same flow in, while the level is at the setpoint.

## Slide 24: Problem 2: steady state error
With P control, once the error has reached a value where is equal to the flow out, the level will stabilize. But it will be different to the setpoint

## Slide 25: P control problem summary
Problem 1: oscillations
  P control will give us oscillations in some processes, regardless of the value of the gain parameter.
Problem 2: steady state error
  P control cannot give us a nonzero value of the control at zero error for some types of process

## Slide 26: Solving P control’s problems
How to get rid of steady state error?
Let’s ignore the present for the moment and concentrate on what has happened in the past

## Slide 27: Solving steady state error: ‘the Past’
Let’s look at the error in the past
SP
MV
+
-
e
Σ
Process
Future
Past
Proportional
u

## Slide 28: Solving steady state error
We can examine how the controller error has evolved in the past
If we sum up the past values of the error, we can get a value that increases when there is a constant error

## Slide 29: Integral Action
We can let the control be given by the sum of past values of the error, scaled by some gain.
In continuous time the sum is an integral:

## Slide 30: Integral Action
SP
MV
+
-
e
Σ
Process
Future
Integral
Proportional
u

## Slide 31: Integral gain, Integral time
Here is where confusion can start…
We have an integral gain which converts an integrated error to a control signal
We would actually like to parameterize this as a time, as in how fast we can remove a steady state error

## Slide 32: Integral gain, Integral time
Let’s rewrite:
As:
is our Proportional Gain, and is our Integral Time

## Slide 33: The Integral time
Why do we use both and here?
Let’s add the proportional and integral parts:

## Slide 34: Proportional and Integral Controller
SP
MV
+
-
e
Σ
Process
Future
Integral
Proportional
u

## Slide 35: Proportional and Integral Controller = PI Controller
We can rewrite the control law:
is the gain parameter, is the time it takes to fix a steady state error

## Slide 36: Solving P control’s problems revisited
We solved the steady state error by adding integral action (summing the past)
How can we solve the oscillation problem?
Let’s look at the future!

## Slide 37: Solving oscillations: ‘the Future’
Let’s look at the error in the future
SP
MV
+
-
e
Σ
Process
Future
Integral
Proportional
u

## Slide 38: Solving oscillations: ‘the Future’
How do we predict the future of the error?
Look at its gradient!
If the gradient (the time derivative) of the error is in a direction that makes the error smaller, we can reduce the control input

## Slide 39: Damping
It can be easier to think of this as damping, something that resists velocity
Think of the wheel on your car…

## Slide 40: Damping
The spring is a proportional controller for the wheel position. The damper adds a derivative action by opposing the velocity of the wheel

## Slide 41: Derivative action
Let’s let the control be dependent on the derivative of the error:
Here is the derivative gain. Let’s again split this into , where is the derivative time

## Slide 42: Derivative action
SP
MV
+
-
e
Σ
Process
Derivative
Integral
Proportional
u

## Slide 43: PID Controller!
SP
MV
+
-
e
Σ
Process
Derivative
Integral
Proportional
u

## Slide 44: Derivative Time
Why do we want as a parameter?
We can think of it as how far ahead we want to predict!
Easier to relate to process

## Slide 45: Problems with Derivative action
We know that a derivative amplifies quick changes.
We can get problems if MV is noisy.
Solution is to add low pass filter

## Slide 46: Derivative with filter
We already have:
Equations will get messy if we add a filter in time domain! Let’s use Laplace! Then we can use algebra instead of calculus.

## Slide 47: Derivative with filter
Laplace transform frequency variable s is also an operator. Multiplication by s is derivation, and division is integration. So the derivative part is now

## Slide 48: Derivative with filter
We add a low pass filter:
Now we have another parameter which is the filter bandwidth. So introducing derivative action requires two more parameters!

## Slide 49: Full PID equation
The complete PID controller now looks like:

## Slide 50: Full PID equation
This simplifies to:

## Slide 51: ISA PID Form
This is the ISA ‘standard form’ for a PID
We have one gain, and three time constants

## Slide 52: The UNICOS PID Controller
Features and quirks

## Slide 53: UNICOS PID Features
Uses the ISA standard equation we just derived
Parameterized by , , ,
Includes limits and ramps on setpoint and output
Can use scaling on input, or both input and output

## Slide 54: UNICOS PID Modes
Point to note:
Manual Mode is not open loop!
Use Output positioning to set
open loop control output

## Slide 55: UNICOS PID Output Calculation
Note the scaling!

## Slide 56: UNICOS PID Scaling
The scaling features are a little tricky, and have important consequences when tuning the controller!
Need to be very careful when applying tuning results! (More on this later!)

## Slide 57: Scaling types
There are three types of scaling
  No scaling
  Input scaling
  Input and output (Full) scaling

## Slide 58: No Scaling
This is the simplest. The inputs and outputs are applied directly to the PID equation, so it operates on engineering values. For example the MV and SP may be temperatures, and the output a power command to a heater

## Slide 59: Input Scaling
Here the input is scaled from engineering values to a normalized value in the range 0-100%. Scaling parameters must be provided. For example 0 bar and 10 bar could be the low and high limits, which are then mapped to 0% and 100% as seen by the PID algorithm.

## Slide 60: Full Scaling (Input and Output)
The input is converted to a 0-100% signal as before, and now the output of the controller is converted from 0-100% to engineering values before being applied to the process

## Slide 61: Scaling Pitfalls
Note that the values of SP, MV and controller output you see in the faceplate are NOT the same as the PID equation ‘sees’ if you use scaling!
If you change the scaling type you MUST scale your controller parameters ()!

## Slide 62: Manual PID Tuning

## Slide 63: P, PI, PD, PID?
For the complete PID controller we have 4 parameters , , ,
But we can also choose to use only parts of the controller, for example just, PI, giving 2 parameters to choose.
How do we know when to use what?

## Slide 64: The Process Model
We now know exactly what’s inside our controller, but so far we haven’t said anything about what’s inside our process!
To be able to tune the controller, we need to know something about it.

## Slide 65: Open Loop Step Response
A good starting point is to make an open loop step test on the process
Note that this is a step on the controller output, not on the setpoint!

## Slide 66: Open Loop Step Response
If our step response looks something like this, we have a stable system with a first order response

## Slide 67: First Order System
We can get 3 pieces of information about the process:
Process Gain
Time Constant
Time Delay

## Slide 68: Process Gain
This is the ratio of the change in MV to the change in control input
In this case is (20-10)/(5-0) = 2

## Slide 69: Time Constant
This is the ‘speed’ of the process.
To read it from the trend, look for the time it takes for the MV to rise to 63% of its final value

## Slide 70: Time Constant
Ok, why 63%??
Because is about 0.63….
The step response is so after time
this is

## Slide 71: Time Delay
This is simpler, it is just the time it takes from the start of the step until the MV starts to move.

## Slide 72: First order process model
We have 3 parameters that determine behavior
determines how big the output change will be
determines how long the process takes to get there
determines how long it takes before the process starts doing anything at all

## Slide 73: Implications for control
The key feature is the relation betweenand
If is small and is big, control using PI is fine
If is similar in size to , we may need a more complex controller (PID)
If is big relative to , PID will struggle; it will integrate during the delay and then see a large jump!

## Slide 74: Mini Exercise: PIDSim
Play with the process model
Try open loop steps
What happens with large delay times?
What happens when adding an integrator?

## Slide 75: Tuning for a first order process
We have a process that looks like
And we know what , and are from our step test. Let’s say that we want our controlled system to behave like this, but with a time constant

## Slide 76: Tuning for a first order process
Now we know what our closed loop should look like, and we also know what the process looks like, and what the controller looks like. We ca use the closed loop relation:
Where is our controller.

## Slide 77: Tuning for a first order process
From here we can work out what controller parameters we need!
This is called Internal Model Control (IMC)

## Slide 78: Internal Model Control (IMC)
Once we do the math, we get these parameters for PI:
(this is Skogestad’s IMC, S-IMC)

## Slide 79: Internal Model Control (IMC)
IMC rules are nice, because they are not just heuristics: they are calculated from a desired behavior.

## Slide 80: Integrating processes
What happens when the step response is a ramp?
Process contains an integrator!

## Slide 81: SIMC tuning rules
The rules can be derived for a number of different process models
http://folk.ntnu.no/skoge/publications/2012/skogestad-improved-simc-pid/PIDbook-chapter5.pdf

## Slide 82: SIMC for UNICOS PID
Point to note: SIMC rules apply for a ‘cascade’ PID structure, not the ISA standard used by UNICOS. For PI and PD they are the same, but for the full PID we need to do a transformation of the parameters:
, ,

## Slide 83: Other tuning rules
There are MANY other sets of tuning rules!

## Slide 84: Ziegler-Nichols
You may have come across Ziegler-Nichols
  Early work (1942)
  Actually developed for fast setpoint tracking, so they are really too aggressive for process control!
  We will revisit them later!

## Slide 85: Tuning rule warning
Lots of tuning rules are based on heuristics, which might only fit certain process types. In addition, you need to be sure what controller structure they are for. You also need to know what the control aim is (setpoint following, disturbance rejection)

## Slide 86: Recommendation: SIMC
SIMC is good because:
  It forces you to do a step test and learn about the process
  You can adjust the rules with an intuitive parameter
  They are easily derived and therefore understood

## Slide 87: Recommendation: SIMC
Recommendation is to start with SIMC.
If you’re still not happy, you can use it as a baseline, and make manual adjustments from there.
Let’s now make a tuning ‘recipe’!

## Slide 88: Tuning ‘recipe’
Step 1: Preparation:
  Make sure it’s ok to put the process into open loop
  Make sure the process is settled (steady state)
  Make sure you are close to your normal operating point

## Slide 89: Tuning ‘recipe’
Step 2: Open loop step test
  Put the controller into Output Positioning
  Make a small step in the output value
  Observe the MV, make sure it doesn’t hit the limits!
  Once the MV has settled, make a step back to where you started.
  Put the controller back in regulation

## Slide 90: Tuning ‘recipe’
Step 3: Calculate process parameters
  Find , and
    (watch out for scaling!)
    is the time taken to rise to 0.63
    is the time between your step input and the first change in MV

## Slide 91: Tuning ‘recipe’
Step 4: Calculate controller parameters
  Use SIMC: choose closed loop time
  Apply tuning rules:

## Slide 92: Tuning ‘recipe’
Step 5: Set parameters and test
  Apply the new parameters in the controller
  Make a small set point change and see how the controller reacts
  If too aggressive, increase and recalculate parameters
  If too slow, decrease and recalculate parameters

## Slide 93: Exercise: Manual tuning in UNICOS

## Slide 94: Hints! Input and I/O scaling
Input Scaling
Find from the trend
Calculate new :
I/O Scaling
Find ,
Calculate new :

## Slide 95: Autotuning
The UNICOS Autotuning tool

## Slide 96: Autotuning
What is autotuning?
  It is NOT a system which continuously updates the controller parameters (this is adaptive control)
  It is just a set of tools to automate the procedure of finding a set of parameters

## Slide 97: Open vs Closed Loop
In our manual tuning we did an open loop experiment (step test) and found parameters from there. This procedure can be automated
There are also methods that allow us to keep the loop closed

## Slide 98: Automated SIMC Tuning
Let’s revisit the SIMC method
Doing the calculations and keeping track of the scaling was a pain
The UNICOS autotuner automates most of this for us

## Slide 99: UNICOS SIMC Autotune
Open the controller faceplate and go to Autotune
Select SIMC (1)
First, we need to identify the process parameters (2)
1
2
3
4

## Slide 100: UNICOS SIMC Autotune
We enter a step size, and it performs the step test, stopping when MV has settled.

## Slide 101: UNICOS SIMC Autotune
Now we select the closed loop response time (3)
This gives us the proposed parameters (4)
We can apply them to the controller (unless set by APAR; these must be set manually)
1
2
3
4

## Slide 102: Closed Loop Autotuning
What if we want to remain in closed loop when tuning?
We can use the Relay Method
Effectively exchanges the PID for an on/off control

## Slide 103: Relay Method
Control only has 2 values, depending on whether MV is higher or lower than SP
Gives a square wave oscillation

## Slide 104: Relay Method: detail
Control goes between and from its original value, with some hysteresis

## Slide 105: Relay Method: detail
Output oscillates with an amplitude
We get two pieces of information from this: Ultimate gain and Ultimate Period

## Slide 106: Relay Method: calculation
Ultimate gain comes from the amplitude of the fundamental frequency of the square wave
Ultimate Period is just the period of the resulting oscillation

## Slide 107: Relay Method: tuning
Again we have MANY rules to choose from.
Ziegler-Nichols are the most well known
Time delay and time constant similar
Integrator and time delay system
Time delay dominated system

## Slide 108: UNICOS Relay Autotuner
The current version uses the Ziegler-Nichols rules
You may find the result too ‘aggressive’
You can always ‘detune’ by reducing and increasing by small amounts

## Slide 109: UNICOS Relay Autotuner
Select method RELAY and controller type (1)
We need to give an amplitude (2). Before starting, we should be in steady state. Then we can input Max and Min values (ideally symmetric!)
2
1
3
4

## Slide 110: UNICOS Relay Autotuner
We also need to give the number of cycles (2). 3 to 5 is usually enough.
Start the relay experiment (3)
2
1
3
4

## Slide 111: UNICOS Relay Autotuner
Popup opens. Observe that we get a nice square wave with fairly constant period.
After the given number of cycles, it will stop automatically

## Slide 112: UNICOS Relay Autotuner
Ziegler-Nichols tuning rules are applied internally. There is no user parameter
Results are displayed (4) and we can choose to apply the new parameters
2
1
3
4

## Slide 113: UNICOS Relay Autotuner
Practical notes:
The experiment begins by checking for steady state. It may take some time before the relay cycles start
If the experiment starts far from steady state, it can cause problems

## Slide 114: Iterative Feedback Tuning
IFT tries to adjust the control parameters in order to minimize a cost function
We won’t look at it in detail here
1
2
3
4

## Slide 115: Exercise: Autotuning in UNICOS
Let’s try out the SIMC and Relay methods
Compare the results to your results from manual tuning
Can you improve the autotuning results?

## Slide 116: Thanks for your attention!